## 33kV & 11kV Standing Load
S.No | Feeder Type / Protection | Relay type | Continous standing load / DC burden (W) | Quantity |  | Total Wattage | Diversity Factor | Actual Load | Remarks
|  |  |  | Relays | Feeders
33kV System
1 | 33kV Incomer Cable Feeder
In Relay Panel
| Line Differential Relay | RED 670 | 50 | 1 | 2 | 100 | 1 | 100
| Directional O/C + E/F Relay | REF 615 | 14.1 | 1 | 2 | 28.2 | 1 | 28.2
| Trip Circuit Supervision Relay | 7PG1753 | 2 | 2 | 2 | 8 | 1 | 8
| Indicating Lamps and Aux. Relays | - | 2 | 5 | 2 | 20 | 0.5 | 10
| Supply Supervision Relay | 7PG1741 | 1.25 | 2 | 2 | 5 | 1 | 5
In LV Compartment
| Bay Control & Protection Unit | REF 545 | 25 | 1 | 2 | 50 | 1 | 50
| Indicating Lamps and Aux. Relays | - | 2 | 5 | 2 | 20 | 0.5 | 10
2 | 33kV Transformer Feeder
In Relay Panel
| Transformer Differential Relay | RET 670 | 50 | 1 | 2 | 100 | 1 | 100
| REF Relay | RET 615 | 11.9 | 1 | 2 | 23.8 | 1 | 23.8
| SBEF Relay | REF 615 | 14.1 | 1 | 2 | 28.2 | 1 | 28.2
| Directional O/C and E/F | REF 615 | 14.1 | 1 | 2 | 28.2 | 1 | 28.2
| Trip Circuit Supervision Relay | 7PG1753 | 2 | 2 | 2 | 8 | 1 | 8
| Indicating Lamps and Aux. Relays | - | 2 | 5 | 2 | 20 | 0.5 | 10
| Supply Supervision Relay | 7PG1741 | 1.25 | 2 | 2 | 5 | 1 | 5
In LV Compartment
| Bay Control & Protection Unit | REF 545 | 25 | 1 | 2 | 50 | 1 | 50
| Indicating Lamps and Aux. Relays | - | 2 | 5 | 2 | 20 | 0.5 | 10
3 | 33kV Bus Section
In Relay Panel
| O/C +E/F Relay | REF 615 | 14.1 | 1 | 1 | 14.1 | 1 | 14.1
| Over Voltage Relay | REF 615 | 14.1 | 1 | 1 | 14.1 | 1 | 14.1
| Trip Circuit Supervision Relay | 7PG1753 | 2 | 2 | 1 | 4 | 1 | 4
| Supply Supervision Relay | 7PG1741 | 1.25 | 2 | 1 | 2.5 | 1 | 2.5
| Indicating Lamps and Aux. Relays | - | 2 | 5 | 1 | 10 | 0.5 | 5
In LV Compartment
| Bay Control & Protection Unit | REF 545 | 25 | 1 | 1 | 25 | 1 | 25
| Indicating Lamps and Aux. Relays | - | 2 | 5 | 1 | 10 | 0.5 | 5
4 | 33kV Busbar Protection Panel
| BBP Relay | DAD-N | 27 | 1 | 2 | 54 | 1 | 54
| CT Supervision Relay | 6RA206 | 3 | 1 | 2 | 6 | 1 | 6
| Supply Supervision Relay | 7PG1741 | 1.25 | 5 | 2 | 12.5 | 1 | 12.5
| Indicating Lamps and Aux. Relays | - | 2 | 5 | 2 | 20 | 0.5 | 10
5 | AVR Panel + Parallel Interlock
| Eberlie AVR Relay | REG D | 15 | 1 | 2 | 30 | 1 | 30
| Bay Control Unit | REC 670 | 50 | 1 | 1 | 50 | 1 | 50
| Supply Supervision Relay | 7PG1741 | 1.25 | 1 | 1 | 1.25 | 1 | 1.25
6 | UPS Load:
Consist of the following:
| PC Industrial Server 4 Nos - 300 W each |  | 300 | 4 | 1 | 1200 | 1 | 1200
| PC Engineer Work Station 1 No - 300 W |  | 300 | 1 | 1 | 300 | 1 | 300
| PC Operator Work Station 1 No - 300 W |  | 300 | 1 | 1 | 300 | 1 | 300
| Monitors 2 Nos - 70 W each for Operator Wrk Stn |  | 70 | 2 | 1 | 140 | 1 | 140
| Monitors 2 Nos - 70 W each for Engg Wrk Stn |  | 70 | 2 | 1 | 140 | 1 | 140
| Service Modem |  | 9 | 1 | 1 | 9 | 1 | 9
| Event Printer Matrix 2 Nos |  | 53 | 2 | 1 | 106 | 1 | 106
| Hardcopy Printer Laser 1 No |  | 75 | 1 | 1 | 75 | 1 | 75
7 | DC Load:
SCMS
| Ruggedcom RSG 2100 |  | 28 | 13 |  | 364 | 1 | 364
| GPS Receiver Meinberg |  | 35 | 2 |  | 70 | 1 | 70
| Insys Modem |  | 10 | 2 |  | 20 | 1 | 20
| SACO 16D1 |  | 25 | 6 |  | 150 | 1 | 150
| Fall Back Switch KU13.1 |  | 2 | 2 |  | 4 | 1 | 4
8 | Common Alarm Panel
| Bay Unit | REC 670 | 50 | 1 | 1 | 50 | 1 | 50
| Alarm Annunciator | SACO64D4 | 20 | 2 | 1 | 40 | 1 | 40
| Alarm Annunciator | SACO16A3 | 20 | 1 | 1 | 20 | 1 | 20
| Door Lamp | - | 5 | 1 | 1 | 5 | 1 | 5
9 | TARIFF METERING PANEL
| Tariff Metering Unit (For 33kV) | ZMQ | 4 | 4 | 1 | 16 | 1 | 16
11kV System
1 | 33/11kV Transformer Incomer Feeder
(LV Compartment)
| Bay Control and Protection Unit | REF 545 | 25 | 1 | 2 | 50 | 1 | 50
| O/C +E/F Relay | REF 615 | 14.1 | 1 | 2 | 28.2 | 1 | 28.2
| Trip Circuit Supervision Relay | 7PG1753 | 2 | 2 | 2 | 8 | 1 | 8
| Supply Supervision relay | 7PG1741 | 1.25 | 1 | 2 | 2.5 | 1 | 2.5
| Indicating Lamps and Aux.Relays | - | 2 | 5 | 2 | 20 | 0.5 | 10
2 | 11kV Outgoing Cable Feeder
(LV Compartment)
| Bay Control and Protection Unit | REF 545 | 25 | 1 | 10 | 250 | 1 | 250
| O/C +E/F Relay | REF 615 | 14.1 | 1 | 10 | 141 | 1 | 141
| Indicating Lamps and Aux.Relays | - | 2 | 5 | 10 | 100 | 0.5 | 50
| Trip Circuit Supervision relays | 7PG1753 | 2 | 2 | 10 | 40 | 1 | 40
| Supply Supervision Relay | 7PG1741 | 1.25 | 1 | 10 | 12.5 | 1 | 12.5
3 | 11kV Bus Section
(LV Compartment)
| Bay Control and Protection Unit | REF 545 | 25 | 1 | 1 | 25 | 1 | 25
| O/C +E/F Relay | REF 615 | 14.1 | 1 | 1 | 14.1 | 1 | 14.1
| Under Voltage Relay | REF 615 | 14.1 | 2 | 1 | 28.2 | 1 | 28.2
| Synchro check | 7VK611 | 5 | 1 | 1 | 5 | 1 | 5
| Trip Circuit Supervision Relay | 7PG1753 | 2 | 2 | 1 | 4 | 1 | 4
| Supply Supervision relay | 7PG1741 | 1.25 | 1 | 1 | 1.25 | 1 | 1.25
| Indicating Lamps and Aux.Relays | - | 2 | 5 | 1 | 10 | 0.5 | 5
4 | 11kV Auxiliary Transformer Feeder
(LV Compartment)
| Bay Control and Protection Unit | REF 545 | 25 | 1 | 2 | 50 | 1 | 50
| O/C +E/F Relay | REF 615 | 14.1 | 1 | 2 | 28.2 | 1 | 28.2
| Trip Circuit Supervision Relay | 7PG1753 | 2 | 2 | 2 | 8 | 1 | 8
| Supply Supervision Relay | 7PG1741 | 1.25 | 1 | 2 | 2.5 | 1 | 2.5
| Indicating Lamps and Aux.Relays | - | 2 | 5 | 2 | 20 | 0.5 | 10
5 | 11kV Busbar protection Panel
| BBP Relay | DAD-N | 27 | 1 | 2 | 54 | 1 | 54
| CT Supervision Relay | 6RA206 | 3 | 1 | 2 | 6 | 1 | 6
| Supply Supervision Relay | 7PG1741 | 1.25 | 5 | 2 | 12.5 | 1 | 12.5
| Indicating Lamps and Aux.Relays | - | 2 | 5 | 2 | 20 | 0.5 | 10
6 | LVAC PANEL
| O/C + E/F | REF 615 | 14.1 | 1 | 3 | 42.3 | 1 | 42.3
| SBEF | REF 615 | 14.1 | 1 | 2 | 28.2 | 1 | 28.2
| Under Voltage Relay | REF 615 | 14.1 | 2 | 2 | 56.4 | 1 | 56.4
| Trip Circuit Supervision Relay | 7PG1753 | 2 | 1 | 3 | 6 | 1 | 6
| Supply Supervision Relay | 7PG1741 | 1.25 | 1 | 3 | 3.75 | 1 | 3.75
| Annunciator | - | 16 | 1 | 1 | 16 | 1 | 16
| Indicating Lamps | - | 2.5 | 10 | 2 | 50 | 1 | 50
| Bay Control Unit | REC 670 | 50 | 1 | 1 | 50 | 1 | 50
7 | Tariff Metering Panel
| Tariff Metering Unit (For 11kV) | ZMQ | 4 | 2 | 2 | 16 | 1 | 16
| Total | [6 empty] | 4841.45
|  |  |  | L1 Continuous Standing Load Current = |  |  |  | 44.0132 | amps @ 110V DC
When i select Relay type column (RED 670 or 615 etc.,)i get all information below the combo box.