## A
Wire Sizer by Solarray, Inc. | Yellow boxes for User Input, check all yellow settings
Copyright 2008, all rights reserved | before double checking with your own final hand calculation
All calculations based on NEC 2005, chapter 9, table 8
Enter Operating Voltage | 204 | Volts (use array MPP voltage for MPPT controllers)
Enter Operating Current | 5.2 | amps
Wire distance | 195 | one way in feet
125% of PV short ciruit Amps | 6.5 | amps
Power | 1060.8 | watts
Cross sectional area | 0.8mm2 | 2mm2 | 3.3mm2 | 5.3mm2 | 8.4mm2 | 13.3mm2 | 21.1mm2 | 33.6mm2 | 42.4mm2 | 53.5mm2 | 67.4mm2 | 107.2mm2
Wire Gauge | 18 | 14 | 12 | 10 | 8 | 6 | 4 | 2 | 1 | o | oo | oooo
Volts Lost | 13.7389 | 5.5128 | 3.4736 | 2.1775 | 1.3583 | 0.88136 | 0.55474 | 0.34736 | 0.27651 | 0.21948 | 0.17454 | 0.10818
Voltage drop | 6.735% | 2.702% | 1.703% | 1.067% | 0.6658% | 0.432% | 0.2719% | 0.1703% | 0.1355% | 0.1076% | 0.08556% | 0.05303%
Final Voltage | 190.2611 | 198.4872 | 200.5264 | 201.8225 | 202.6417 | 203.1186 | 203.4453 | 203.6526 | 203.7235 | 203.7805 | 203.8255 | 203.8918
Power lost (watts) | 71.4421 | 28.6667 | 18.0627 | 11.3229 | 7.0633 | 4.5831 | 2.8846 | 1.8063 | 1.4378 | 1.1413 | 0.90763 | 0.56255
Efficiency | 93.27% | 97.3% | 98.3% | 98.93% | 99.33% | 99.57% | 99.73% | 99.83% | 99.86% | 99.89% | 99.91% | 99.95%
Cost of Lost power | 571.5371 | 229.3338 | 144.5018 | 90.5832 | 56.5067 | 36.6646 | 23.0772 | 14.4502 | 11.5026 | 9.1302 | 7.261 | 4.5004
Pick a Gauge based on:
NEC 156% current (PV only) | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK
very conservative
125% NEC load current | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK
Normal Code, 24 hour cont. rating
Electric Vehicle, 1 hr rating | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK
to not melt insulation
Cost effectiveness | go bigger | go bigger | OK | over sized | OK | over sized | over sized | over sized | over sized | over sized | over sized | over sized
is cost of larger wire worth power gains
Comparable Cost of wire(2 x distance + etc) | 58.5 | 97.5 | 140.9 | 196.1 | 205 | 400 | 519 | 717 | 875 | 1190 | 1787 | 2965
Cost of connectors, extra time,etc per circuit | 0 | 0 | 0.5 | 5 | 10 | 10 | 12 | 15 | 17 | 20 | 32 | 40
Cost of wire per ft. THHN single | 0.15 | 0.25 | 0.36 | 0.49 | 0.5 | 1 | 1.3 | 1.8 | 2.2 | 3 | 4.5 | 7.5
weight of wire per 1000 ft | 4.92 | 12.4 | 19.8 | 31.4 | 50 | 79.5 | 126 | 201 | 253 | 319 | 403 | 641
resistance of wire per 1000 ft.@167 degF | 7.95 | 3.19 | 2.01 | 1.26 | 0.786 | 0.51 | 0.321 | 0.201 | 0.16 | 0.127 | 0.101 | 0.0626
NEC ampacity of THHN | 14 | 25 | 30 | 40 | 55 | 75 | 95 | 130 | 150 | 170 | 195 | 260
NEC Temp Compensated Ampacity | 14 | 25 | 30 | 40 | 55 | 75 | 95 | 130 | 150 | 170 | 195 | 260
(80%rated) normal breaker size | 15 | 15 | 20 | 30 | 40 | 60 | 100 | 125 | 150 | 175 | 200 | 250
max. ampacity | 18 | 35 | 40 | 55 | 80 | 105 | 140 | 190 | 220 | 260 | 300 | 400
Advanced User Inputs:
Temperature of wire in degrees F | 85 |  |  | Temperature Coefficient (Ohms) |  | 0.85215
Temperature of Air in degrees F | 85 |  |  | Temperature Coefficient (Amps) |  | 1
Cost of Copper per lb. | 1
Installed Cost of PV per watt | 8 | Used in cost of lost power calc.
Hours/ day at selected current | 6 | set to 6 for PV wiring, set to 1 for inverter rating, set to 0.5 for surge calculations, set to 24 for continuous loads, etc .
MPPT controller? | 1 | set to 0 for PV w/o MPPT , set to 1 for MPPT or for Non PV circuits also.